#### Electrical System Diagram

| Disconnect size in amps |  | Size of copper service wire | Size of conduit |  | Size of aluminum service wire | Size of conduit | Size of ground wire |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 100 |  | #4 | 1 ¼ “ |  | #2 | 1 ¼ “ | #6 |
| 150 |  | #1 | 2” |  | 2/0 | 2” | #6 |
| 200 |  | 2/0 | 2” |  | 4/0 | 2” | #4 |